## Sheet1
Serial No. | Description | Valve Identification details (Model,etc.) | Location / Main Equipment | Nominal Diameter (mm) | Set Pressure (MPa) | Temperature (C) | Medium | Discharge method | Total Nos. of Safety valves | valve Outlet pressure Mpa | Design Pressure of vessle / Mpa | 3% | back pressure 10%
1 | BFP booster pump inlet line safety valves | A 41H -25 | 0 m level / 6.3m level | 25 | 1.31 | <300 | Water | atmosphere | 3 | 0.1 | 1.2 | -8.3969 | 7.6336
2 | Gland steam line safety valves (LP turbine side) | A 48Y-16C | 6.3 M legve / Near Jacking oil pumps | 150 | 0.28 | 350 | Air/steam | atmosphere | 2 | 0.1 | working pressure 42kpa | #VALUE! | 35.7143
6 | LP heater 8/7 vent line safety valve | A 41H- 40 | 6.3 m level / LP heaters 8/7 | 25 | 3.95 | 200 | Air/water | atmosphere | 1 | 0.1 | 4 | 1.2658 | 2.5316
7 | LP heater 6 vent line safety valve | A 41H -40 | 6.3 m level / LP heaters 6 | 25 | 3.95 | 200 | Air/water | atmosphere | 1 | 0.1 | 4 | 1.2658 | 2.5316
8 | HP heater 3 safety valve | A 48Y-4 | 6.3 m level / HP heater 3 | 100 | 2.09 | 215 | Air/steam | atmosphere | 1 | 0.1 | 2.2 | 5.2632 | 4.7847
9 | LP heater 6 safety valve | A47H-16C | 6.3 m level / LP heater6 | 100 | 0.59 | 350 | Air/steam | atmosphere | 1 | 0.1 | 0.6 | 1.6949 | 16.9492
10 | Condensate extraction pump inlet safety valves | A 42 Y-16C | 0 m level / Condensate Extraction system | 25 | 0.3675 | <300 | Water | atmosphere | 2 | 0.1 | working pressure 0.15Mpa | #VALUE! | 27.2109
12 | CCCW heat Exchanger(Demin side) | A 47H-16C | 0 m level / CCCW Heat Exchangers | 100 | 1.3 | <425 | Air/Demin water | atmosphere | 2 | 0.1 | 1.25 | -3.8462 | 7.6923
13 | CCCW heat Exchange (sea water side) | A 47 H-16P | 0 m level / CCCW Heat Exchangers | 100 | 0.7 | <200 | Air/Sea water | atmosphere | 2 | 0.1 | 1.25 | 78.5714 | 14.2857
14 | LP Heater 5 safety valve | A 47 H -16C | 12.6 m level / LP heater 05 | 100 | 0.5 | 350 | Air/Steam | atmosphere | 1 | 0.1 | 0.6 | 20 | 20
15 | LPH 5 Vent safety valve | A 41 H - 40 | 12.6 m level / LP heater 05 | 25 | 3.95 | 200 | Air/Water | atmosphere | 1 | 0.1 | 4 | 1.2658 | 2.5316
16 | HP Heater 2 safety valve | A 48 Y - 3 | 12.6 m level / HP heater 02 | 100 | 4.56 | 258.3 | Air/Steam | atmosphere | 1 | 0.1 | 4.8 | 5.2632 | 2.193
17 | HP Heater 1 safety valve | A 48 Y -10 | 12.6 m level / HP heater 01 | 100 | 7.315 | 289 | Air/Steam | atmosphere | 1 | 0.1 | 7.7 | 5.2632 | 1.3671
18 | Auxiliary Header safety valve | A 48 Y -25 | 16.6 m level / Auxiliary header | 250/300 | 1.68 | 350 | Air/Steam | atmosphere | 1 | 0.1 | 1.7 | 1.1905 | 5.9524
19 | Deaerator Tank and Deaerator | A 48 Y -25 | 18.9 m level / Deaerator | 150/200 | 1.17 | 350 | Air/Steam | atmosphere | 4 | 0.1 | 1.2 | 2.5641 | 8.547
20 | HP heater 03 Feed water inlet safety valve |  | Upper area CCCW pumps | 20 | 26.13 | 572 | Steam | atmosphere | 1 | 0.1 | 27.5 | 5.243 | 0.3827
Note on F18: Cold Differential Test Pressure (CDTP) -26.68MPa -EA Turbine unit 02